## Slide 1: Syska Welcome Slide
Presented by Brandon Henson and Samuel Payne 2025

## Slide 2
Brandon Henson, PE, CPD
Supervising Plumbing Engineer
Introduction
Samuel Payne, PE
Project Manager / Mechanical
Engineer of Record

## Slide 3
Overview
Ranked Among the Top Engineering Firms by ENR, CSE, BD+C and EC+M
Specialized Healthcare Practice Area
Leader in High-Performance Design
Culture of Innovation and Award-Winning Engineering
Early Adopter of BIM/3D Modeling and MEP Enhancements

## Slide 4: Agenda: FGI Code – 2026 Draft Changes
FGI – History and Why (1 minute – Sam)
Current Code (2022)  New Code (2026)
Plumbing Supply
Plumbing Drainage
Medical Gas
** These are the proposed changes in the draft 2026 FGI code and will be voted on later this year for adoption

## Slide 5: Plumbing: Domestic Water Distribution

## Slide 6: FGI 2026 Code Updates: Fixture Counts
IBC/IPC as reference
2022
2026
Redefined fixture count tables
Aligns with patient acuity and use case
Key Change
  Adjusted Plumbing fixture minimums based on department use and space function
  Next slide show example – drawing to highlight a change. Show table

## Slide 7: FGI 2026 Code Updates: Plumbing
Plumbing
  2022 Code: IPC or local code compliance
  2026 Draft: Requires nationally recognized code, clarifies IPC adoption
Importance
  Aligns code expectations nationwide
  Use a specific example for audience interaction
  UPC, municipal codes

## Slide 8: FGI 2026 Code Updates: Handwashing Stations
Strict placement rules at entry
2022
2026
Replaced requirement of "one for every 4 patient care stations or fewer and for each major fraction thereof " with "at least one HW station provided in rooms with multiple patient care stations."
Added requirement for one additional HW station for every 4 patient care stations and for each major fraction thereof.
Key Change
  Handwashing requirements are tailored to clinical risk and workflow
  Next slide show example – find graphics

## Slide 9: Handwashing stations– example – in drawing or discussion?

## Slide 10: FGI 2026 Code Updates: Water Heater Sizing
General guidance for sizing in patient areas
2022
2026
Emphasizes recovery rates and redundancy in critical areas.
Show in a table/matrix
Key Change
  More prescriptive language for critical care and surgical areas

## Slide 11: FGI 2026 Code Updates: Legionella Mitigation
Risk Management required
2022
2026
Adds system recirculation and no dead-ends
diagram
Key Change
  Expanded infection prevention controls

## Slide 12: FGI 2026 Code Updates: Hot Water Temp Control
Mentions anti-scale protection
2022
2026
Expands on scale prevention with specific max outlet temperatures
Give examples
Add a table for this
Key Change
  Tighter limits on outlet temp in patient-accessible areas (max 120degF)

## Slide 13: FGI 2026 Code Updates: Water Supply Capacity
General fixture approach
2022
2026
Diversity factor for >1000 units
Example? Use flush valve Hunter curve
Key Change
  Recognizes high-volume fixture area

## Slide 14: FGI 2026 Code Updates: Emergency Water Supply
Not addressed
2022
2026
Requires plan, backup system and emergency power
Example?
Key Change
  Enhances hospital disaster resilience
  Talk more about resilience? Resiliency VSHE.pptx

## Slide 15: FGI 2026 Code Updates: Emergency Plumbing
Covers basic redundancy
2022
2026
Emphasizes on continuity planning for water/sewer failures
Walk through process, mention Hurricane Helene, and how not a lot of facilities had provisions to emergency water.
Key Change
  New requirements for emergency potable water sources in critical care
  Next slide - example

## Slide 16: FGI 2026 Code Updates: Infection Control
IPC vaguely addresses
2022
2026
Direct guidance on drainage layouts to avoid cross-contamination
Give examples – provide further information
Key Change
  Stronger exmphasis on plumbing design as part of infection control strategy which should be coordinated with facility manager and dedicated team

## Slide 17: FGI 2026 Code Updates: Dialysis Water Connection
Mentioned under patient treatment areas
2022
2026
Dedicated section with layout and redundancy requirements
Provide layout on this slide and walk through
Key Change
  Adds design specifications for safe water delivery in dialysis units.

## Slide 18: FGI 2026 Code Updates: Valve Requirements
Valves
  Mains
  Risers
  Branches
2022
2026
Adds
  Tagging
  Schedule
  Stop Valves
Key Change
  Improves system maintenance and documentation

## Slide 19: FGI 2026 Code Updates: Backflow Prevention
Based on AWWA M14
  What is this?
2022
2026
Expands scope, cites IAPMO for specific device use
Key Change
  Creates stronger alignment with national backflow codes.

## Slide 20: Plumbing: Drainage Systems

## Slide 21: FGI 2026 Code Updates: Backflow Prevention
Based on AWWA M14
  What is this?
2022
2026
Expands scope, cites IAPMO for specific device use
Key Change
  Creates stronger alignment with national backflow codes.

## Slide 22: Medical Gas Systems
Proposed Revisions for 2026

## Slide 23: FGI 2026 Code Updates: Medical Gas
General Medical Gas
  Proposed additions:
  2.1-8.4.4.3 Instrument air systems. Instrument air systems shall produce air of a quality that complies with ANSI/ISA S7.0.01 Quality Standard for Instrument Air.

## Slide 24: FGI 2026 Code Updates: Medical Gas
General Medical Gas
  Proposed revisions of Table 2.1-3: Oxygen, Vacuum, Medical Air, WAGD, and Instrument Air Systems (Outlets/Inlets)

## Slide 25: FGI 2026 Code Updates: Medical Gas
Table 2.1-3 Oxygen, Vacuum, Medical Air, WAGD, Inst. Air,
  Proposed deletions:
    Airborne Infection Isolation (AII) Room
      Medical Air & O2 deleted (removed requirement).
    Protective Environment Room (2.2-2.2.4.4):
      Medical Air & O2 deleted (removed requirement).
    Airborne Infection Isolation (Intensive Care) Room
      Room type removed from table
    Pediatric Intensive Care Unit (PICU) Room
      Room type removed from table
    Observation unit patient care station (2.2-3.3.2):
      Medical Air deleted (removed requirement).
    Endoscopy procedure room (2.2-3.11.2):
      Medical Air deleted (removed requirement).
    Endoscopy pre-/post-procedure patient care area (2.2-3.11.3):
      Oxygen/Vacuum now shown as “—8” (portable permitted); piped outlets deleted

## Slide 26: FGI 2026 Code Updates: Medical Gas
Table 2.1-3 Oxygen, Vacuum, Medical Air, WAGD, Inst. Air,
  Proposed additions:
    Phase I PACU (2.1-3.4.4): Increased Vacuum from 2/station → 3/station.
    Phase II Recovery (2.1-3.4.5): Added footnote 7 clarification: If combined with PACU, must have 3 vacuum outlets per bed/station.
    Triage room (2.2-3.1.3.3 (2)): Added footnote 8 allowing portable source availability.
    Low-acuity patient care station (2.2-3.1.3.6 (6)): Oxygen and Vacuum both noted as “—8”, meaning a portable source shall be available (new option).
    Interior human decontamination room (2.2-3.1.3.6 (7)(a)): Updated Vacuum requirement to “—1,9”, allowing portable vacuum equipment.

## Slide 27: FGI 2026 Code Updates: Medical Gas
Table 2.1-3 Oxygen, Vacuum, Medical Air, WAGD, Inst. Air,
  Proposed additions:
    Endoscope processing room (2.2-3.11.4.2 / .3): Added Instrument Air requirement with footnote 12 (vacuum and/or instrument air if needed).
    Sterile processing rooms (2.1-5.1.2.2 & .3): Added Instrument Air requirements, with footnotes 10, 11 clarifying portable compressed air and NFPA 99 guidance
    Added Medical Air – 1/bed (previously not required)
      Rehabilitation unit hospital patient room (2.6-2.2.2)
    Added Footnote:
      The provision of medical gases shall also comply with NFPA 99: Healthcare Facilities Code. The clinical risk assessment in NFPA 99 may result in more stringent requirements for location's where this table permits use of portable gases.
    Added verbiage to Footnote 2:
      Where inhalation anesthesia, or analgesia, including nitrous oxide, will be used, a waste anesthesia gas disposal (WAGD) system shall be provided. Use of portable delivery and scavenging equipment shall be permitted in lieu of a permanently installed WAGD system.
    Revised footnote 10: (Removed portable compressed air and added nitrogen)
      In the one-room sterile processing facility and the clean workroom of the two-room sterile processing facility, an instrument air outlet or nitrogen, portable compressed air shall be provided as required by the equipment used.